## 6.6kV-SG
Sample Load Schedule for Light Fixture Factory
Load Type | Equipment Description | C - Continous I - Intermittent S - Standby | Bus | Volt (kV) | Power (kW) | Efficiency | Power Factor | Continous (C) |  | Intermitttent (I) |  | Standby (S) |  | Frequency(Hz) | F.L Current (A)
[8 empty] | kW | kVAR | kW | kVAR | kW | kVAR
M | Light LED Equipment 1 | C | A | 6.6 | 500 | 0.85 | 0.85 | 500 | 569.1664 |  |  |  |  | 50 | 60.5397
M | Light LED Equipment 2 | C | A | 6.6 | 500 | 0.85 | 0.85 | 500 | 569.1664 |  |  |  |  | 50 | 60.5397
M | Light LED Equipment 3 | S | B | 6.6 | 500 | 0.85 | 0.85 |  |  |  |  | 500 | 569.1664 | 50 | 60.5397
M | Robot 1 | C | A | 6.6 | 2000 | 0.85 | 0.85 | 2000 | 2276.6654 |  |  |  |  | 50 | 242.1588
M | Robot 2 | S | B | 6.6 | 2000 | 0.85 | 0.85 |  |  |  |  | 2000 | 2276.6654 | 50 | 242.1588
P | 415V-SG-BUS A |  | A | 6.6 |  |  |  | 100 | 113.8333 | 10 | 11.3833 |  |  | 50
P | 415V-SG-BUS B |  | B | 6.6 |  |  |  | 100 | 113.8333 |  |  |  |  | 50
|  | Continous (C) |  | Intermittent (I) |  | Standby (S)
|  | kW | kVAR | kW | kVAR | kW | kVAR
| Loading of Bus A | 3100 | 3528.8314 | 10 | 11.3833 | 0 | 0
| Loading of Bus B | 100 | 113.8333 | 0 | 0 | 2500 | 2845.8318
| Total Loading of Switchgear | 3200 | 3642.6647 | 10 | 11.3833 | 2500 | 2845.8318
| Loading Factors | a |  | b |  | c
|  | 1 |  | 0.3 |  | 0.1
| Continous Load with Load Factor | 3200 | 3642.6647
| Intermittent Load with Load Factor |  |  | 3 | 3.415
| Largest Intermittent Load |  |  | 10 | 11.3833
| Standby Load with Load Factor |  |  |  |  | 250 | 284.5832
| Largest Standby Load |  |  |  |  | 2000 | 2276.6654
| Peak Demand | [6 empty] | kVA |  | Power Factor | 0.65998
|  | 3200 | 3642.6647 | 10 | 11.3833 | 2000 | 2276.6654 | 7894.141
| Max Demand | 3200 | 3642.6647 | 10 | 11.3833 |  |  | 4863.7606
| Selected Transformer Rating in MVA | 8/10 (ONAN/ONAF)

## 415V-SG
Sample Load Schedule for Light Fixture Factory
Load Type | Equipment Description | C - Continous I - Intermittent S - Standby | Volt (kV) | Bus | Power (kW) | Efficiency | Power Factor | Continous (C) |  | Intermitttent (I) |  | Standby (S) |  | Frequency(Hz) | F.L Current (A)
[8 empty] | kW | kVAR | kW | kVAR | kW | kVAR
M | Light enclosure Manufacturing Equipment | C | 0.415 | A | 100 | 0.85 | 0.85 | 100 | 113.8333 |  |  |  |  | 50 | 192.56
M | Automatic Checking Machine | C | 0.415 | B | 100 | 0.85 | 0.85 | 100 | 113.8333 |  |  |  |  | 50 | 192.56
P | Power Socket | I | 0.415 | A | 10 | 0.85 | 0.85 |  |  | 10 | 11.3833 |  |  | 50 | 19.256
|  |  | Continous (kW) |  | Intermittent (kW) |  | Standby (kW)
|  |  | kW | kVAR | kW | kVAR | kW | kVAR
|  | Loading of Bus A | 100 | 113.8333 | 10 | 11.3833 | 0 | 0
|  | Loading of Bus B | 100 | 113.8333 | 0 | 0 | 0 | 0
|  | Total Loading of Switchgear | 200 | 227.6665 | 10 | 11.3833 | 0 | 0
|  | Loading Factors | a |  | b |  | c
|  |  | 1 |  | 0.3 |  | 0.1
|  | Continous Load with Load Factor | 200 | 227.6665
|  | Intermittent Load with Load Factor |  |  | 3 | 3.415
|  | Largest Intermittent Load |  |  | 10 | 11.3833
|  | Standby Load with Load Factor |  |  |  |  | 0 | 0
|  | Largest Standby Load |  |  |  |  | 0 | 0
|  | Peak Demand | [6 empty] | kVA |  | Power Factor | 0.65998
|  |  | 200 | 227.6665 | 10 | 11.3833 | 0 | 0 | 318.1899
|  | Max Demand | 200 | 227.6665 | 10 | 11.3833 |  |  | 318.1899
|  | Selected Transformer Rating in kVA | 400